## COMPREHENSIVE
Topic | Type | Inspection | Task | Priority |  |  | Frequency
|  |  |  | I | II | III | D | MO | QTRLY | YRLY
A1010 -Standard Foundation | Cracks & Separation | Check that there are no cracks or separations in the walls if the structure is new. | [7 empty] | Y
|  | Check that the observed cracks or separations are no more than hairline if the structure is used and is less than 10 years old. | [7 empty] | Y
|  | Check that the observed wall cracks or separations are no more than 1/8" wide if the structure is more than 10 years old. | If the observed cracks or separations are wider than nominal, check the structure for causes such as settling, and make appropriate repairs. | [6 empty] | Y
|  | Check that vertical expansion joints in brick are uniform in width. | [7 empty] | Y
|  | Check vertical expansion for seal integrity. | If the vertical expansion joints show signs of failing as described, check the structure for settling, or seal shrinkage and make the appropriate repairs. | [6 empty] | Y
| Drainage | Check that water does not pool near the foundation after a heavy rain. | If it does, bring in fill and re-grade or add an underground drainage system with area drains. | [6 empty] | Y
|  | Check that the grade slopes away from the foundation at least 1 inch vertical per foot, horizontally for the first 5 feet all around the perimeter (may be less where paving occurs). | If necessary, revise the grade with sandy clay (not sand alone) fill or add underground drainage. | [6 empty] | Y
|  | Check that where paving occurs near the structure, that it positively drains away from the foundation. | Add underground drainage with area drains or re-pave. | [6 empty] | Y
|  | Check that gutters and downspouts are clean and water from downspouts is directed away from the foundation. | [6 empty] | Q
|  | Keep accurate records of the number of catch basins cleaned and the amount of waste collected. | This will allow you to determine if landscaping is contributing to the blockage. Trimming or removal of some landscaping may be necessary. | [6 empty] | Y
|  | Clean catch basins, storm drain inlets, and other conveyance structures in high pollutant load areas just before the wet season. | Schedule annually in August or September. | [6 empty] | Y
|  | Check that gutters and downspouts are clean with no blockages and are tied directly into an underground drainage system. | If downspouts or the drainage system is blocked, determine where the blockage occurs (underground camera if necessary) and use snake or jitter to open the blockage. If not on an underground system, have above ground extensions (for example, flexible plastic pipe or long concrete splash block) to carry the water at least five to ten feet away from the building before it is allowed to run onto the soil. (Does not apply if the soil is known to be predominately non-expansive.) | [5 empty] | Q
| Vegetation | Check that there is no broadleaf tree (for example; oak, ash, maple, alder, poplar) closer to the foundation than a distance equal to the height of the tree, even if the tree is on an adjacent property. (Does not apply if the soil is known to be predominately non-expansive.) | If long existing trees are closer than nominal, consider trimming back the tree to inhibit root growth or consult an arborist. Keep a close eye on the foundation in these areas. | [6 empty] | Y
|  | Check that there is no conifer tree (for example; pine) closer to the foundation than a distance equal to the radius of its canopy, even if the tree is on an adjacent property. (Does not apply if the soil is known to be predominately non-expansive.) | If long existing trees are closer than nominal, consider trimming back the tree to inhibit root growth or consult an arborist. Keep a close eye on the foundation in these areas. | [6 empty] | Y
|  | Check that there are no trees of any kind and no large shrubs growing next to the foundation. (Does not apply if the soil is known to be predominately non-expansive.) | Remove if possible. | [6 empty] | Y
|  | Check that the automatic sprinkler system (if applicable) is properly functioning. | Change settings as required to keep watering uniform but to a minimum(as needed to support the vegetation), particularly around the foundation. Set the cycle times to purposely water trees away from the structure in an effort to establish their roots away from the foundation. Irrigations should be installed and adjusted as to not spray on buildings. |  |  |  |  | M
|  | Check for vegetation in front of fresh air intakes. | If found, remove vegetation. | [5 empty] | Q
| Water Leaks | Check that swimming pools, ponds, and fountains hold water without leaking. | If losing water, check for leakage on supply and return lines. If no leakage is found in the pond, it may need to be drained to find the leak. | [6 empty] | Y
|  | Check that there are no leaks near the foundation, such as a faucet drip or a condensate drip from an air conditioning unit. | If found, repair as needed. | [5 empty] | Q
A2020 - Walls for subgrade enclosure | A2020 - Walls for subgrade enclosure | Check that the observed cracks or separations are no more than hairline if the structure is used and is less than 10 years old. | [7 empty] | Y
|  | Check to see if there is water penetration into basement. | [5 empty] | M
|  | Check that the grade slopes away from the foundation at least 1 inch vertical per foot, horizontally for the first 5 feet all around the perimeter (may be less where paving occurs). | [7 empty] | Y
|  | If possible check that exterior of wall has waterproofing. | [7 empty] | Y
A4010 - Standard Slabs on Grade | Slab Integrity | Walk the interior and verify pad is level. Check that there are no uncomfortable floor slopes, easily noticed by walking each room | If you suspect it to be out of level during a walk through, use a 4' to 6' level or laser level to check for slope. If out of level, search for the reason why. Re-engineering may be needed.
|  | Look for moisture seeping up through concrete pad: discoloration, blistering of the flooring, swelling and lifting of the flooring. | Check for the source of the moisture and effect repairs
|  | Keep floors well sealed. | Repair floor cracks, joints, and scaling, chipping or flaking.
A4040 - Pits and Bases | Piers and Equipment bases; Pits | Check for water penetration.
Check for settling.
B1010 - Floor Construction | Dimensional Lumber Joists | Walk the interior and verify that the floor is level.
Check that there are no uncomfortable floor slopes.
Check for squeaks or soft spots.
Check for doors that may be sticking.
| Wood Truss | Walk the interior and verify that the floor is level.
Check that there are no uncomfortable floor slopes.
Check for squeaks or soft spots.
Check for doors that may be sticking.
| Post & Beam with Decking | Walk the interior and verify that the floor is level.
Check that there are no uncomfortable floor slopes.
Check for squeaks or soft spots.
Check for doors that may be sticking.
| Pre-stressed concrete | Look for moisture seeping through concrete.
Look for discoloration.
Look for blistering of the flooring.
Look for swelling and lifting of the flooring.
| Metal & Concrete | Look for moisture seeping through concrete.
Look for discoloration.
Look for blistering of the flooring.
Look for swelling and lifting of the flooring.
Check to see if there are any areas where rusting may be visble.
B1020 - Roof Construction | Dimensional Lumber Joists | Site along from soffit to ridge looking for sags.
Check for raised areas indicating detached or swelled sheathing.
Site along facia looking for sags.
If accessible from the attic look for signs of water intrusion or rot.
| Wood Truss | Site along from soffit to ridge looking for sags.
Check for raised areas indicating detached or swelled sheathing.
Site along facia looking for sags.
If accessible from the attic look for signs of water intrusion or rot.
| Pre-stressed concrete | Look for moisture seeping through concrete: discoloration, blistering, and rust.
| Metal & Concrete | Look for moisture seeping through concrete; discoloration, blistering, and rust.
B1080 - Stairs | Wood | Check that tread and rise are remaining consistent in spacing.
Check that stairs are not squeaking or sagging.
Check that hand railings are securely fastened.
| Concrete | Check for settling.
Check that hand railings are securely fastened.
| Metal | Check welds for cracking and any bolts for loosening.
Check that hand railings are securely fastened.
| Masonry | Check for Cracks.
Check for settling.
Check that hand railings are securely fastened.
B2010 - Exterior Walls | Masonry | Check bricks, blocks and mortar for cracks and loose joints. | Re-point joints and seal cracks.
|  | Check for efflorescence seeping from walls. | Check for areas where water might be entering into the masonry and seal any areas found. Clean efflorescence areas and re-seal or re-paint.
|  | Check the condition of caulking where the masonry meets other materials. | Repair caulking if necessary.
|  | Watch for vandalism. | Keep a record of the last anti-graffiti application if used. Make sure that it is kept up to date. Remove any vandalism as soon as possible after it occurs (one hour response time recommended).
| Siding | Check siding for loose or missing pieces, lifting or warping, and popped nails. | Re-attach where necessary.
|  | Check painted surfaces for paint failure (peeling, chipping, blistering, chalking), water damage, or mildew. | Thoroughly clean and prepare affected areas, and repaint with anti-mildew additive if necessary.
|  | Check the condition of caulking where two different materials meet, such as where wood siding joining the foundation wall, at inside corners, and where window and door trim meets the siding. | Repair caulking if necessary.
| Trawled on Surfacing | Check for damaged corners or for areas that have been damaged due to heavy blows. | Thoroughly clean and prepare affected areas, and repair surface with the appropriate materials.
|  | Check surfaces for material failure (peeling, chipping, blistering, chalking, panel warping or separation from structure). | Determine the reason for structure failure and make subsurface repairs. Repair the surface with the appropriate materials.
Check for water damage, or mildew.
|  | Check the condition of caulking. | Repair caulking if necessary.
B2020 - Exterior Windows | Window Integrity | Check the condition of caulking where siding or other wall material meets the window casing. | Repair as needed.
|  | Check the windows for cracked or broken glass. | Repair broken panes, and replace broken glass.
|  | Check for loose putty around the panes. | Replace cracked putty with glazing compound.
Check for holes in screens.
|  | Check for evidence of moisture between panes. | Replace windows where the gas charge has been compromised.
|  | Check that windows close and seal properly. | Adjust where possible or add weather stripping.
|  | Check curtain wall systems for proper drainage. | Make repairs where needed.
B2050 - Exterior Doors and Grilles | Door Integrity | Make sure that all doors work properly for example, they do not stick, are not warped and swing freely without binding. | Trim doors or shim jambs where possible to improve fit. Severely warped doors should be replaced.
|  | Examine that all door lock hardware works easily. | Lubricate keyways and latch sets annually.
|  | Check weather stripping and thresholds on doors for damage and tightness of fit. | Repair or replace as needed.
|  | Check door closers for proper operation and hydraulic fluid leaks | Replace badly leaking closers. Adjust swing speed, back check, and latch rate annually.
B2070 - Exterior Louvers and Vents | Louvers | Check to insure that louvers are securely fastened.
Check that the vanes are straight.
Check that interior insect screens are intact.
If louvers are operable, check the operation.
| Vents | Check to insure that vents are securely fastened.
Check that interior insect screens are intact.
B3010 - Roofing | Inspection | Fall restraint systems, inspected annually, and used during inspections. | Install new system if none is present.
|  | Roofing shall be inspected biannually, spring and fall. | Create a spreadsheet and establish specific dates for the inspections (for example, third week of September).
|  | Inspect penetrations including, but not limited to, flue stacks, chimneys, HVAC roof curbs and duct work, gas lines, electrical conduit, and roof drains shall be checked for watertight seal. | Reseal any damaged areas.
|  | Inspect for ponding of water on flat roof areas. | Make repairs to the roof that will allow the water to run to gutters, drains, or scuppers to prevent future deterioration of roof surfaces and possible problems with indoor air quality.
|  | Check gutters, drains and downspouts for debris and leaking joints. | Remove debris and reseal cracked joints.
|  | Perform indoor air quality inspections. | Log the results and compare with local or national standards.
|  | Inspect for missing or damaged roof vents. | Replace where needed.
| Flat Roof/Membrane | Check that there are no cracks or separations in the coverings. | Reseal if cracks or separations are found. Cracks, broken bubbles and separations need to be sealed immediately using manufacturers recommended sealants.
| Composite Shingle | Check for roof warping. | Check from the attic (where accessible) to see if there are broken or rotted rafters or if the sheathing has pulled away from the rafter. Make repair as needed. Replace failed sheathing as necessary.
|  | Check shingles for granular loss, buckling or curling, missing tabs or ridge caps. | If damage is severe or extensive, replace the affected shingles.
|  | Remove heavy moss build up. | Remove moss by pressure washing or use an approved moss killer.
| Metal | Check for deterioration or corrosion of horizontal panel seams, vertical panel seams, panel fasteners and perimeter and penetration flashings.
Check for loose, missing or dried sealant.
Check Panel termination at the eaves, ridges and valleys to ensure closure strips are in place.
Check for buckling or standing water at the laps of the panels.
|  | Check metal roofs for screws, fasteners, and panels that may have worked loose due to the expansion and contraction of the roof. | Tighten screws, refasten panels and flashing and reseal where necessary using only sealant recommended by the manufacturer.
B3020 - Roof Appurtenances | Antennas | Check to ensure that poles have not slipped down to penetrate roof covering.
Check guy wire stays to make sure they are not pulling out of the roof and causing damage.
| Cupolas | Check that curbs are not penetrated.
Check any flashing to see that it is functioning properly.
Check for buildup of debris around base.
| Signs | Check to ensure that sign supports are not penetrating roof covering.
Check guy wire stays to make sure they are not pulling out of the roof and causing damage.
| HVAC units | Check that curbs are not penetrated.
Check flashings.
Check that condensate drains are not damaging roof coverings and are properly draining.
Check for buildup of debris around unit.
| Exhaust fans | Check that curbs are not penetrated.
Check flashings.
Check for buildup of debris around unit.
B3060 - Horizontal Openings/Penetrations | Chimneys and flues | Inspect flue stacks and chimneys. | Reseal any damaged areas.
| Ducts | Inspect for missing or damaged roof vents. | Replace where needed.
| Vent Pipes | Inspect for missing or damaged vent flashing or boots. | Repair or replace where needed.
| Drains | Check gutters, drains and downspouts for debris and leaking joints. | Remove debris and reseal cracked joints.
| Skylights | Inspect for broken panes and dislodged flashing.
B3080 - Overhead Exterior Enclosures | Awnings | Inspect awnings for penetrations.
Check for loose connections.
Check supports to insure that they are securely anchored, stable and free from deterioration.
Check for accumulated debris.
| Covered waiting areas | Inspect roof coverings for penetrations.
Check for loose connections.
Check supports to insure that they are securely anchored, stable and free from deterioration.
Check for accumulated debris.
| Gazebos | Inspect gazebo roofs for penetrations.
Check for loose flashings.
Check for accumulated debris.
Check supports to insure that they stable and free from deterioration.
C1010 - Interior Partitions | GWB on wood or metal studs | Inspect for damaged GWB.
Check for nails popping.
Check for signs of moisture or mold.
GWB on metal studs
Masonry
CMU
Operable walls
C1020 - Interior Windows | Door lights
Visibility
C1030 - Interior Doors | Wood
Metal
Roll up
Partitions (accordion, restroom)
| Lock hardware | Check that handles move freely and that the key ways work easily.
Check that the strike enters the strike plate without binding.
Inspect for any loose parts.
| Door closers | Check for leaking oil.
Check swing, latch and back-check for proper speeds.
Inspect mounting screws and swing arm connections for looseness.
C1040 - Interior Grilles and Grates | Grills & Grates | Check to insure that grills are securely fastened and free of damage or accumulated debris.
Check grates to make sure they are intact and secured.
Make sure that the tines are straight and properly gapped.
C1060 - Raised floor construction | Access Flooring | Walk the interior and verify that the floor is level.
Check that there are no uncomfortable floor slopes.
Check for squeaks or soft spots.
Check for doors that may be sticking.
| Platform/stage floors | Walk the interior and verify that the floor is level.
Check that there are no uncomfortable floor slopes.
Check for squeaks or soft spots.
Check for doors that may be sticking.
C1070 - Suspended Ceiling Const. | C1070 - Suspended Ceiling Const. | Check that there are no sags in the ceiling.
Check that grills and sprinkler head escutcheons are in place.
Check to insure that T-bars are not bent or twisted.
Check to insure that lights are safely wired or chained.
Check for stained ceiling tile indicating leaks.
C2010 - Wall Finishes | Brick or Masonry | Check for sheer cracks. | Cracks or chipped masonry may be difficult to repair. Mortar can be re-pointed. If the wall is severely out of plumb or cracked, replacement should be explored.
Check for chipping or flaking paint.
Check for settling or separations.
Check for loosened or missing mortar.
Check for water penetration.
Check for bulging or out of plumb.
| GWB and Paint | Check for sheer cracks. | Repair as needed and repaint.
Check for nail or screw popping.
Check for holes.
Check for chipping or flaking paint.
Check for settling or separations.
Check for water penetration.
Check for bulging or out of plumb.
| GWB with Coverings | Check for sheer cracks. | Vinyl covering will need to be repaired or replaced depending upon the severity of the damage.
Check for nail or screw popping.
Check for holes.
Check for cut or peeling material.
Check for settling or separations.
Check for water penetration.
Check for bulging or out of plumb.
| CAB | Check and report any damage immediately. | CAB should be removed from circulation spaces if possible. It can be managed in place but care must be taken whenever work is done around CAB and damaged CAB should be treated as a hazmat incident.
Check for chipping or flaking paint.
Check for settling or separations.
Check for water penetration.
Check for bulging or out of plumb.
| Wainscotting | Check for separation from GWB. | Repair as needed and repaint.
Check for nail or screw popping.
Check for water penetration.
Check for bulging or out of plumb.
| Chair Rails | Check for separation from GWB. | Repair as needed and repaint.
Check for nail or screw popping.
Check for chipping or flaking paint.
C2020 - Interior Fabrications | Plaster wall systems | Check for nail or screw popping.
Check for water penetration.
Check for bulging or out of plumb.
| Wood cornice, base & window trim | Check mitre joints for tightness.
Check for water damage and mold.
Check that molding are secure in place.
C2030 - Flooring | Slab Flooring | Walk the interior and verify pad is level. | If you suspect it to be out of level during walk through, use a 4'to 6' level, or laser level to check for slope. If out of level, search for reason why. Re-engineering may be needed.
Check that there are no uncomfortable floor slopes, easily noticed by walking each room.
|  | Look for moisture seeping up through concrete pad. | Check for the source of the moisture and effect repairs.
Look for discoloration and blistering of the flooring.
Look for swelling and lifting of the flooring.
|  | Keep floors well sealed. | Repair floor cracks, joints, scaling, chipping, and flaking.
| Carpet | Check for wear, stains, fraying, delamination and odors. | For wear areas, see if it is possible to change the traffic pattern. Effect repairs to carpet as soon as they are discovered as this will keep them from expanding.
|  | Look for color loss, rippling, pilling, soiling. | This may be a manufacturers warranty claim depending on the age of the carpet. Check warranty.
|  | Check for seam separation. | This could be an installation warranty item. Check warranty. Make repairs as soon as possible to prevent the spread of the damage.
| Vinyl | Look for discoloration from mold and mildew and asphalt tracking. | This might indicate that there is moisture penetrating from under the flooring. Make every effort to find the source to prevent the mold from spreading. These areas will need to be replaced.
|  | Check for stains or scuffing. | Scuffs and stains are very difficult to remove from vinyl flooring. Replacement may be necessary if the damage is too extensive.
|  | Verify there are no seam separations, buckling, cuts, gouges or indentations. | This could be an installation warranty item. Check warranty. Make repairs as soon as possible to prevent the spread of the damage.
| Laminate | Look for buckling, cupping, seam swelling or gaps.
|  | Check for discoloration, peaked seams, cuts and gouges, fading, loss of gloss, indentations, scratches, stains and burns. | Moisture and wear patterns are the most common sources of floor covering problems. Where problems occur, make every effort to find the source. Make repairs as soon as possible to prevent the spread of the damage. Replacement may be necessary if the damage is too extensive.
| VCT & Vinyl Tile | Inspect for gaps, buckling and discoloration. | See maintenance action suggestions for vinyl and laminate.
| Ceramic & Porcelain Tile | Inspect for slippage. | Many ceramic floor tiles are designed to be slip resistant. Waxing over them can negate this design feature.
|  | Check for chipping, splitting, crazing, porosity, cracked grout and porous surface. | Clear loose pieces from affected areas and reinstall with the appropriate adhesives and then re-grout. Apply silicone grout sealer to dried grout. Remove any silicone residue from tile surfaces.
Check for adhesive failure.
| Gym Floors - Wood | Inspect for tightening, cupping, shrinkage and broken pieces of wood. | Moisture is the main cause of infrastructure damage to gym wood floors. It can be very costly. Check for sources of moisture on a regular basis. Remove debris for expansion. Void to allow the floor to expand and contract.
|  | Verify HVAC settings. | Set to maintain a consistent temperature and relative humidity between 35 and 50.
|  | Verify walk off mats are in place at all outside entrances. | Industry standards say that it takes about 16 feet of matting to remove most of the soil brought in from the outside.
|  | Look for scratches and other damage to surface. | Do not allow the use of chairs, tables or other equipment on the floor without a protective covering for the floor.
|  | Verify floor has sufficient sealant. | Floor should be screened and re-sealed annually and resurfaced every ten years.
C2040 - Stair Finishes | Paints and epoxies | Check for areas of excessive wear.
Check that pained surfaces are not flaking.
| Concrete | Check for excessive cracking or chipping.
Check that efflorescence is not present.
| Rubber | Check to insure that treads and risers are securely adhered.
Checks for cuts or gouges in treads.
| Metal | Check for cracks in welds.
Check for excessive wear.
C2050 - Ceiling Finishes | Open | Check for water stains, and peeling paint. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to detemine the cause and then effect repairs.
Check for excessive dust build up on pipes, beams, ducts, etcetera.
|  | Monitor escutcheons around sprinkler heads, diffusers, light fixtures and other equipment to ensure they are secure and sealed. | Check that wires or chains are attached to light fixture to prevent falling in the event of an earthquake.
| Painted GWB | Check for water stains. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to detemine the cause and then effect repairs.
Look for soft spots, and peeling paint.
Check for discoloration around light fixtures.
Verify access hatch in large hard-lid ceilings are large enough for appropriate access and/or per building code.
|  | Monitor escutcheons around sprinkler heads, diffusers, light fixtures and other ceiling mounted equipment are secure and sealed. | Check that wires or chains are attached to light fixture to prevent falling in the event of an earthquake.
| Tile | Check for water stains. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to detemine the cause and then effect repairs.
Check for soft spots, and peeling paint.
Check for discoloration around light fixtures.
Verify access hatch in large hard-lid ceilings are large enough for appropriate access and/or per building code.
|  | Monitor escutcheons around sprinkler heads, diffusers, light fixtures and other ceiling mounted equipment, make sure they are secured and sealed. | Check that wires or chains are attached to light fixture to prevent falling in the event of an earthquake.
| Suspended | Check for water stains, discoloration around light fixtures, soft spots, sages, and peeling paint. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to detemine the cause and then effect repairs.
|  | Check panels in suspended T-bar grids for bent or sagging sections. | Repair or replace.
Check panels in suspended T-bar grids are set well in place to reduce falling during seismic event.
Verify access hatch in large hard-lid ceilings are large enough for appropriate access and/or per building code.
|  | Monitor escutcheons around sprinkler heads, diffusers, light fixtures and other ceiling mounted equipment to ensure they are secured and sealed. | Check that wires or chains are attached to light fixture to prevent falling in the event of an earthquake.
D1010 - Vertical Conveying Systems | Elevator | Check to see that annual L&I inspections have been done.
| Dumb waiter | Check to see that annual L&I inspections have been done.
| Wheelchair lift | Check to see that annual L&I inspections have been done.
D2010 - Domestic Water Distribution | Supply | Check fixtures for blueish or rust colored stains.
|  | Take note of the inside of supply lines when changing fixtures. | Apply proper water treatment.
|  | Check that hot water supply lines are insulated. | Repair/replace the insulation with approved materials and adhesives.
|  | Listen for signs of ‘water hammer’. | If water hammer exists, check that arresters are not flooded. Drain shock arrestors or replace.
|  | Check circulation, pump lubrication, and couplers. | Lubricate pumps.
|  | Check backflow prevention valves and that the certification is current. | Schedule for re-certification if out of certification.
|  | Check water heaters for proper temperatures, T & P valves are working properly, and that gas heaters are properly vented. Check for leaks or rust at the base of heaters. | Replace T & P relief valve if leaking, clean out venting if plugged, replace water heater if leaking.
|  | Check to make sure that fixture shutoffs function properly. | Tighten stem, repair valve seats if leaking. When opening gate type valves, turn half turn after opening all the way so that the valve does not seize open.
|  | Make sure that main water shutoffs are properly marked and documented. | Apply valve tags and purpose if missing.
|  | Check that hot water setpoint is properly adjusted. | Adjust setpoint to no more that 120° farenheit.
|  | Check that equipment operating schedules are appropriate (operates during occupied schedules, off or cycles in un-occupied schedule). | Adjust operating times to match occupancy schedule.
D2020 - Sanitary Drainage | Waste | Check P-traps, wax rings, pumps, etcetera for leakage. | Tighten fittings, replace if leaking from holes.
|  | Identify and document the location of cleanouts. | Obtain drawings and mark cleanout locations. Skecth drawings if builidng plans are not available.
|  | Check waste lines that travel a long distance for sagging or lack of slope. | Apply propper support if lacking. Supports include hanger rods with insulated saddles.
|  | Check roof vents annually to see that they are not plugged or are broken off. | Repair or replace.
|  | Check to see that they are not close to intake fans. | Extend pipe up to at least 36 inches above intake or offset 10 feet away and rise up.
D2030 - Building Support Plumbing Systems | Sewer | Check septic system annually or as required by local jurisdictions and document when tanks are pumped. | Schedule if the septic tank service if full.
|  | Check for signs of settling in drain fields. | If this is an old system, this could mean that you have a water leak that has gotten into the drain field. Check water usage for spike in flow. If newly installed, it might be natural compaction due to settleing and fill should be added to level ground.
| Irrigation | Install irrigation meters to avoid sewer charges. | Sewer charges are often tied to potable water usage which would include irrigation systems. Separating irrigation onto its own meter will keep the water being used for irrigation from be counted in the sewer water calculations.
| Fire loop | Check for signs of settling which can indicate a leak.
Check that annual testing is done.
| Bio mass loops | Check for signs of settling which can indicate a leak.
Check that supply and return pressures are within proper ranges.
D2050 - General Services Compressed Air | Fire sprinkler system (exterior) | Test and blow out condesate on compressor on a monthly basis (or as required).
Check compressor oil levels.
Check safety equipment.
Check compressor line dryers.
Check for leaks or excessive compressor cycling.
| Pneumatic controls | Test and blow out condesate on compressor on a monthly basis (or as required).
Check compressor oil levels.
Check compressor line dryers.
Check for leaks or excessive compressor cycling.
Check safety equipment.
Check actuators.
Check systems pressures.
| Vocational Ed systems | Test and blow out condesate on compressor on a monthly basis (or as required).
Check compressor oil levels.
Check compressor line dryers.
Check for leaks or excessive compressor cycling.
Check safety equipment.
D3010 - Facility Fuel Systems | Natural Gas | Check meter and shut off to building.
Always keep alert for gas smells.
| Propane | Check meter and shut off valve to building.
Always keep alert for gas smells.
| Oil | Check fuel filters on a regular basis.
Check to insure that water is not seeping into underground tanks.
Set up auto refill and occaasionally check tank levels.
D3020 - Heating Systems | Steam | Inspect to insure all equipment is operating and that safety systems are in place. | Pay particular attention to high limit cut-offs and water make up switches.
Check steam pressure under different loads.
Check water levels.
|  | Check gas or oil burner flame. | View through the flame viewing window to insure the proper combustion is taking place.
Check motor condition temperature.
|  | Verify that the bottom, surface and water column blow downs are occurring and are effective. | Blowing down the boilers regularly helps prevent the buildup of residue which decreases efficiency.
|  | Keep Daily logs on: type and amount of fuel used; blue gas temperatures; makeup water volume; steam pressure, temperature and amount generated. | TRACK: type and amount of fuel used; blue gas temperature; make-up water volume; steam pressure, temperature and amount generated.
Check and clean/replace filters and strainers on a scheduled basis.
|  | Confirm water treatment is functioning properly. | Sample water weekly.
Check relief valves for leaks.
Inspect boiler insulation.
|  | Check that sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect. Caution: A skilled technician should do this for steam.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
Change air filters on a regular basis.
| Hot Water | Visually inspect to insure all equipment is operating and that safety systems are in place. | Pay particular attention to high limit cut-offs and water make-up switches.
Check water levels.
|  | Check gas or oil burner flames. | View through the flame viewing window to insure the proper combustion is taking place.
Check motor condition temperatures.
|  | Verify the bottom, surface and water column blow downs are occurring and are effective. | Blowing down the boilers regularly helps prevent the buildup of residue which decreases efficiency.
|  | Keep daily logs on:tType and amount of fuel used; blue gas temperatures; make-up water volume. | TRACK: type and amount of fuel used; blue gas temperature; make-up water volume.
Check and clean/replace filters and strainers on a scheduled basis.
|  | Confirm water treatment system is functioning properly. | Sample water weekly.
Check relief valves for leaks.
Inspect boiler insulation.
|  | Check that sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
Change air filters on a regular basis.
| Heat Pumps | Proper refrigerant charge. | Check gages or color indicators that the charge is adequate. The O & M Manual should have this informatin. Add proper refrgerant if low. Caution: A skilled technician should do this for refrigeration.
|  | Check that sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect. Caution: A skilled technician should do this for refrigeration.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
Change air filters on a regular basis.
| Electric | Check sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or Systems manual).
Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule).
Check that fans are operating properly.
Change air filters on a regular basis.
| Bio Mass | Check for signs of settling which can indicate a leak.
Check that supply and return pressures are within proper ranges.
D3030 - Cooling Systems | Heat Pump | Proper refrigerant charge. | Check gages or color indicators that the charge is adequate. The O & M Manual should have this informatin. Add proper refrgerant if low. Caution: A skilled technician should do this for refrigeration.
|  | Check sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or Systems manual). | Measure mdeium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect. Caution: A skilled technician should do this for refrigeration.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy .
| Bio Mass | Check for signs of settling which can indicate a leak.
Check that supply and return pressures are within proper ranges.
| Chillers | Proper refrigerant charge. | Check gages or color indicators that the charge is adequate. The O & M Manual should have this informatin. Add proper refrgerant if low. Caution: A skilled technician should do this for refrigeration.
|  | Check sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or Systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect. Caution: A skilled technician should do this for refrigeration.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
| Cooling Towers | Service system biannually. | Recommended in the spring and fall.
|  | Inspect equipment and repair as needed. | Lubricate motors and bearings as needed; Adjust drive belts and pulleys as necessary; Remove debris from fan blades and check for damage; Adjust make-up water system as necessary.
|  | Clean tank systems to remove scale, dirt, and biological growth. | Remove scale, dirt and biological growth from tank; clean air intake screens and sump strainers; clean spray nozzles.
Clean air intake screens and sump strainers.
Clean spray nozzles.
Water treatments shall be performed by trained personnel only.
Verify all chemicals are stored away from all student occupied areas.
|  | Check that sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
D3050 - Facility HVAC Dist. System | Duct | Chech that insulation wrap is properly attached to the duct, where possible, check that insulation liner is attached to duct. | Repair/replace the insulation with approved materials and adhesives.
| Plenums | Chech that insulation wrap is properly attached to the duct, where possible check that insulation liner is attached to duct. | Repair/replace the insulation with approved materials and adhesives.
|  | Check that access door seals are not leaking. | Repair or replace seals.
| Piping | Check for leaks. | Repair/replace the pipe with approved materials and joining compound.
|  | Check that insulation wrap is properly attached to the duct. Where possible, check that insulation liner is attached to duct. | Repair/replace the insulation with approved materials and adhesives.
| Valves | Check valves for leaks. | Repair/replace the valve or components with approved materials.
D3060 - Ventilation | Fans | Check that bearings are properly lubricated. | Apply appropriate lubrication.
|  | Check belts for wear and adjusted properly. | Replace belts and adjust sheaves.
|  | Check that sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or systems manual). | Measure medium with calibrated instrament at location of sensor. Calibrate or replace if reading is incorrect.
|  | Check that equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
| Ducts | Chech that insulation wrap is properly attached to the duct. Where possible, check that insulation liner is attached to the duct. | Repair/replace the insulation with approved materials and adhesives.
| Natural | Check that the occupant understands how the natural ventilation functions. | Train the occupant how to operate the system.
|  | Check that the sensors are calibrated and control setpoints are properly adjusted (found in controls submittal or systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect.
|  | Check that equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
D4010 - Fires Suppression | Extinguishing systems | Check that extinquishing systems are tested and serviced annually.
| Kitchen Hoods | Check that hoods are tested and serviced annually.
| Sprinklers | Check that sprinklers are tested and serviced annually.
D4030 Fire Suppression Specialities |  | Check that extinquishers are tested and serviced annually.
Check that fire cabinets are being used properly
D5010 - Facility Power Generation | Generator | Set up schedule to check oil levels and fuel supply
Set up test run schedule.
D5020 - Electrical Service and Distribution | Transformers | Check that transformers are secured from the public and that vegitation is removed from around them.
| Vaults | Check that electrical vaults are secured from the public.
Check that worker access is safe.
| Main Subpanels | Check that there is a minumum of 3 feet of clearance in front of all sub-panels.
Check to insure that neutral bars and wires are tight.
Use heat gun to check for hot spots.
Check that sub-panels are secured from the public.
| EMT, wiring | Where visible, check that there are no disconections in EMT.
Where visible, check that there are no box covers off.
| Motors | Check lubricant levels on a regular basis.
Check to insure that there is not a build up of dirt on the casing or vents.
Check pully or other drive connection couplings.
D5030 - General Purpose Electrical Power | Sub-panel to Branch panel wiring; branch panels | Where visible, check that there are no disconections in EMT.
Where visible, check that there are no box covers off.
Check to insure that neutral bars and wires are tight.
Use heat gun to check for hot spots.
D5040 - Lighting | Tubes | Check for lights with discoloration on the ends.
Check for lights that are flickering.
Check for lights that have different spectrums than the rest.
| Ballasts | Check for ballasts that are leaking.
Check for fixtures that are slow to start.
| Lens | Check for clouded or broken lenses.
Check to see that lenses are secure.
Check to see that there is no water in the lenses.
| CFC | Check for lights that are flickering.
Check for lights that have different spectrums than the rest.
| Switches | Check that switches are not intermittent.
Check that switches are not arcing.
Check that switches are not upside down.
| Incandescent | Check that the lights are not super bright.
| HPS, MV, etc. | Check for fixtures that are slow to start.
Check for fixtures that come on and off.
| Occupancy Sensors | Check that the motion sensor are adjusted properly. | Adjust sensitivity of the sensor. Replace if failed.
D5080 - Miscellaneous Electrical Systems | Elevators | Check to see that annual L&I inspections have been done.
| Signs | Check to insure that signs are properly grounded.
Check for corrosion.
Check that all electrical boxes, switches, etcetera are waterproofed.
| Pool Systems | Check to insure that pool systems are properly grounded.
Check for corrosion
Check that all electrical boxes, switches, etc are waterproofed
| Fuel Dispensing Facilities (bus maintenance Facilities) | Check to insure that fuel islands are properly grounded
Check for corrosion.
Check that all electrical boxes, switches, etc are waterproofed.
| Bus Garage | See D5020, D5030 and D5040.
D6010 - Data Communications | Internet | Check system for function, reliability, and speed.
| Wireless connections | Check system for function, reliability, and speed.
| Servers | Check system for function, reliability, and speed.
Check to insure that room AC is working properly.
D6020 - Voice Communications | Land Lines | Check system for function, reliability, and speed.
| Radio Systems | Check system for function, reliability, and speed.
Check antenna tower.
Check radios and charging systems.
D6030 - Audio-Video Communication | Cable | Check system for function, reliability, and speed.
| Satellite | Check system for function, reliability, and speed.
Check that dishes are secure and free of debris.
D6060 - Distributed Comm/Monitoring |  | Check system for function, reliability, and speed.
Check call-out capability is funtioning properly.
D7010 - Access Control and Intrusion Defection | Keypads | Check system for function, reliability, and speed.
Check that key pads have not been vandalized.
| Electronic Locks | Check system for function, reliability, and speed.
D7030 - Electronic Surveillance | Cameras | Check system for function, reliability, and speed.
Check that cameras have not been vandalized.
| Motion Sensors | Check system for function, reliability, and speed.
Check that motion sensors have not been vandalized.
| DVR's | Check system for function, reliability, and speed.
D7050 - Detection and Alarm | Smoke Detectors | Check system for function, reliability, and speed.
Insure that annual testing has occurred, use canned smoke.
| Heat Detectors | Check system for function, reliability, and speed.
Insure that annual testing has occurred.
| Strobes & Horns | Check system for function, reliability, and speed.
Insure that annual testing has occurred.
D8010 - Integrated Automation Facility Controls | DDC | Check system for function, reliability, and speed.
E1010 - Vehicle and Pedestrian Equipment | Hydraulic Lifts | Check to see that annual L&I inspections have been done.
E1030 - Commercial Equipment | Laundry | Check for leaking around equipment.
Check dryer vents for lint buildup.
E1040 - Institutional Equipment | Library | Check with teacher to see if there is broken or damaged equipment.
| Theatre & Stage | Check with teacher to see if there is broken or damaged equipment.
| Laboratory | Check with teacher to see if there is broken or damaged equipment.
E1070 - Entertainment and Recreational Equipment | LCD Projectors (Installed) | Check with teacher to see if there is broken or damaged equipment.
| Screens | Check with teacher to see if there is broken or damaged equipment.
| TV's | Check with teacher to see if there is broken or damaged equipment.
E1090 - Other Equipment | Dishwashers (kitchen) | Check water temperature to insure 180 degree final rinse temperature.
| Walk in freezer | Check that temperature remains around zero degrees farenheit.
| Walk in refrigerator | Check that temperature remains around 34 degrees farenheit.
| Ovens | Check that ovens are being properly cleaned.
| Deep fryers | Check that ovens are being properly cleaned.
| Mixers | Check that mixers are being properly cleaned.
E2010 - Fixed Furnishings | Window treatments | Check that window treatments are functioning properly.
Check for damage to treatments.
| Fixed grills and mats | Check that grills are not clogged.
Check that mats are not worn and are being regularly cleaned.
| Fixed multiple seats | Check that bleachers are functioning properly.
Check that cleaning under bleachers occurs regularly.
| Fixed casework | Check that casework hinges are working properly.
Check that casework latches are working properly.
Check that casework drawer glides are working properly.
E2050 - Movable Furnishings | Library bookshelves | Check casters for smooth functioning.
| Cafeteria tables | Check that torsion assist for raising and lowering tables is functioning properly.
Check that locking systems are working properly.
| Kitchen serving tables | Check casters for smooth functioning.
| Kitchen food warmers | Check casters for smooth functioning.
Check that warmers are properly grounded.
Note on H318: Shellie Neuman: stopped here.